Models:	TLW-CW    Separate set points for VAV cooling and warm up

TLW-C       Separate set point for VAV cooling only

GUIDE SPECIFICATION

(Suitable for Section 23 36 16 Variable-Air-Volume Units of the CSI Master Format)  Material in italics applies only to model TLW-CW. Delete the italics for model TLW-C.

2.2 Thermally Powered VAV Diffusers

- Thermally powered variable air volume diffusers shall be Therma-Fuser™ model TL    manufactured by Acutherm, Hayward CA.

- Thermally powered VAV diffusers shall be a complete VAV terminal and thermostat self-contained in linear sidewall diffuser. They shall be thermally powered with one cooling thermostat/actuator and one changeover thermostat/actuator. External wiring or pneumatics shall not be allowed.

- In the cooling mode the VAV diffusers shall open on a rise in room temperature. The temperature set point shall be separately adjustable between 70°F/21°C and 78°F/26°C. The initial set point shall be factory set at 74°F/23°C.  The changeover thermostat shall be factory installed and adjusted to open the diffuser when the supply air temperature rises above 80°F/27°C and return to the cooling mode when the supply air temperature falls below 68°F/20°C.

- The diffuser and blades shall be constructed of extruded aluminum with all visible portions powder coated. The diffuser shall be complete with plenum constructed of 24-gauge galvanized steel.

- The diffuser shall have an induction chamber and supply air venturi at one end for inducing room air past the room sensing thermostat/actuator. The venturi shall be at least 4 in. / 100 mm wide for effective induction. The VAV diffusers shall have positive induction of secondary room air over the room thermostat/actuator at all flows from fully closed to fully open.

- A power compression spring cartridge shall be attached directly to the thermostat/actuators to contain the forces produced without distorting other parts of the diffuser and assure accuracy of control.

- Optional—The diffuser shall be lined with ½" fiber-free foam insulation adhered with ASTM C 916 adhesive. The insulation and adhesive shall meet the requirements of NFPA 90A and 90 B.

- The manufacturer shall warrant that all VAV diffusers shall be free from defects in materials and workmanship for a period of ten years from date of shipment.

- Supply air to the VAV diffuser shall be constant temperature (may be reset to another constant temperature). Supply air shall be limited to no lower than 50°F/10°C on cooling and no higher than 120°F/49°C on heating. The heating high limit shall be as low as possible but no lower than 80°F/27°C.